## Slide 1: DC-DC Converter for PV Module Integration
Group 760

## Slide 2: CONTENT
INTRODUCTION
CONVERTER DESIGN
MPPT ALGORITHM
TESTS RESULTS
DISCUSSION
CONCLUSION

## Slide 3: Introduction
Notes: Motivation
Existing problems
What is a MIC
Why a MIC
Problem statement

## Slide 4: Motivation
Global need of transition towards clean energy.
Wind and solar energy production as fastest growing method in 2017.
Improve current generation efficiencies.
Slide
of 59
Aitor

## Slide 5: Existing problem
Partial shaded PV panel [2]
Power mismatches:
Production tolerances.
Partial shading.
Cracks.
Uneven aging.
Dirt.
Slide
of 59
Aitor

## Slide 6: What is a module integrated converter (MIC)?
Is a part of each PV module.
Prevents mismatch losses.
Serial or parallel arrangements.
Slide
of 59
Aitor

## Slide 7: Why MICs?
Advantages:
Allows individual maximum power point tracking.
Replaces bypass diode.
Higher system efficiencies achieved under mismatches.
Certain topologies allow bidirectionality.
Disadvantages:
Could imply lower efficiency under specific cases.
Production cost increase.
Slide
of 59
Aitor

## Slide 8: Problem statement and objectives
How can a module integrated converter be designed to maximize
the PV power generation under real conditions?
Objectives:
Design a DC-DC converter for integration with a PV panel.
Implementation of an MPPT algorithm.
Hardware implementation of the MIC.
Test of the system and validation of the MIC.
Slide
of 59
Aitor

## Slide 9
Converter Design

## Slide 10: System requirements
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Slide
of 59
Nicolai
Notes: How did we select the values
Input from PV panel
Output from inverter voltage and # of panels
# of panels from minimum and maximum duties
Ripples so we dont mess with the PV panel

## Slide 11: Selection of topology
Non-inverting buck-boost converter
Slide
of 59
Nicolai
Notes: Capabilities of both higher and lower output voltage
2 or 4 MOSFETs
Bidirectional opportunities
Lower (conduction) losses

## Slide 12: Passive components Sizing
Calculated using the ripples.
Finding worst case conditions.
Depends on switching frequency.
Output capacitor
Slide
of 59
Nicolai
Notes: Did a voltage sweep to determine worst case

## Slide 13: Passive components Sizing
Input capacitor
Inductor
Slide
of 59
Nicolai

## Slide 14: Passive components Selection
Minimum 20% margin was included.
Reused inductor.
Component | Theoretical value | Implemented value | Voltage rating
Input capacitor | 1540µF | 1880µF | 100V
Output capacitor | 130µF | 820µF | 250V
Inductor | 1.3mH | 1.93mH | -
Slide
of 59
Nicolai
Notes: Input cap is 4*470uF
Calculation mistakes lead to wrongly selected cout

## Slide 15: Power circuitry
High frequency capacitors.
Discharging resistors.
Protection diodes.
Slide
of 59
Nicolai

## Slide 16: Driving circuitry
Optocouplers for isolation.
Current limiting resistors.
Decoupling capacitors.
Slide
of 59
Nicolai

## Slide 17: Sensor circuitry
Slide
of 59
Nicolai
Notes: Optical unity-gain amplifier – voltage sensors
Hall effect – current sensor

## Slide 18: Power supplies
External supplies.
Isolated 12V TRACO supplies.
Linear 5V voltage regulator.
LED at every supply line.
Slide
of 59
Nicolai

## Slide 19: PCB layout
Considerations:
Hot and cold sides.
Isolations.
EMI - EMC.
Others.
Slide
of 59
Aitor

## Slide 20: Hot and cold sides
Clear separation of hot and cold sides.
Power side.
Control side, isolated.
Control side, non-isolated.
Slide
of 59
Aitor

## Slide 21: EMI - EMC
Reduced current loops.
Hall sensor location.
Ground planes.
Slide
of 59
Aitor

## Slide 22: Isolations
Isolation gap.
Slide
of 59
Aitor

## Slide 23: Others
Test points.
Other measuring points and user communication.
Heat sink location.
10mm power traces.
Slide
of 59
Aitor

## Slide 24
MPPT Algorithm

## Slide 25: Maximum power point (MPP)
I-V and P-V curves of a generic solar panel
Slide
of 59
Thassilo

## Slide 26: Perturb & Observe technique
P-V curve from a PV panel
1. Power evalution
> moving to MPP
< moving away from MPP
2. Voltage evalution
 | > | <
> | Voltage increase | Voltage decrease
< | Voltage decrease | Voltage increase
 | Voltage increase | Voltage decrease
 | Voltage decrease | Voltage increase
Slide
of 59
Thassilo

## Slide 27: Implementation
Block diagram of the system including the MPPT
Slide
of 59
Thassilo

## Slide 28: Initial MPPT implementation
Top figure: Conversion ratio for buck and boost modes.
Bottom figure: Mapping of the control variable for mode decision.
Mapping for mode decision:
If control variable < 0.5  Buck mode
If control variable 0.5  Boost mode
Incrementing control variable means decreasing PV voltage!
Slide
of 59
Thassilo

## Slide 29: Initial MPPT implementation
Top figure: Conversion ratio for buck and boost modes.
Bottom figure: Mapping of the control variable for mode decision.
Mapping for mode decision:
If control variable < 0.5  Buck mode
If control variable 0.5  Boost mode
Incrementing control variable means decreasing PV voltage!
Slide
of 59
Thassilo

## Slide 30: Initial MPPT implementation
Finite state machine for P&O algorithm
Problems:
“If/else” structure difficult to find errors.
Variable step required more complex code.
Slide
of 59
Thassilo

## Slide 31: Fixed vs variable perturb step – Buck
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.
Slide
of 59
Thassilo

## Slide 32: Fixed vs variable perturb step – Boost
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.
Slide
of 59
Thassilo

## Slide 33: Final implementation
Main issues:
Measurements were read too fast.
Perturb step decreased after false positive MPP detection.
Environmental variables’ changes.
Slide
of 59
Nicolás

## Slide 34: Final implementation
Pmax
Vmax
Perturbation step & condition
change detection FSM
Slide
of 59
Nicolás

## Slide 35: Final implementation
3 seconds sim time
Boost, 8 panels
Slide
of 59
Nicolás

## Slide 36: Converter Design
Test Results

## Slide 37: Testing Overview
Model of the PV panel.
Standard test conditions.
Boundary between modes of operation.
Sudden changes in environmental.
Converter’s efficiency.
…
Slide
of 59
Nicolás

## Slide 38: Test setup
Slide
of 59
Estefanía

## Slide 39: Test setup
PLECs model for interface with the RT Box.
RT Box:
Slide
of 59
Estefanía

## Slide 40: PV panel curves
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
[V] | 36.9 | 36.87 | 36.68 | 36.19
[A] | 8.14 | 6.49 | 4.86 | 3.23
[W] | 300.4 | 239.5 | 178.5 | 117
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
 | 36.9 | 36.87 | 36.68 | 36.19
 | 8.14 | 6.49 | 4.86 | 3.23
 | 300.4 | 239.5 | 178.5 | 117
P-V curves for T=25ºC and varying irradiance.
I-V curves for T=25ºC and varying irradiance.
Irradiance effect:
PV module datasheet (STC)
Slide
of 59
Estefanía

## Slide 41: PV panel curves
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
[V] | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
[A] | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
[W] | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
 | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
 | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
 | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
P-V curves for 1000 W/m2 and varying temperature.
I-V curves for 1000 W/m2 and varying temperature.
Temperature effect:
Slide
of 59
Estefanía

## Slide 42: Standard Test Conditions (STC)
Simulated results under STC with .
Buck mode:
Experimental results under STC with .
Slide
of 59
Estefanía

## Slide 43: Standard Test Conditions (STC)
Simulated results under STC (.
Boost mode:
Experimental results under STC (.
Slide
of 59
Estefanía

## Slide 44: Boundary between modes of operation
Panel’s voltage, current and power under STC (.
Buck mode:
Duty cycles and voltages under STC (.
10 panels
If T>25ºC  Boost
Slide
of 59
Estefanía

## Slide 45: Boundary between modes of operation
Panel’s voltage, current and power under STC (.
Boost mode:
Duty cycles and voltages under STC (.
9 panels
If T<25ºC  Buck
Slide
of 59
Estefanía

## Slide 46: Sudden change in irradiance
Simulated results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Experimental results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Buck mode:
Slide
of 59
Estefanía

## Slide 47: Sudden change in temperature
Simulated results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Experimental results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Buck mode:
Slide
of 59
Estefanía

## Slide 48: Comparison simulation and experiments
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s
Slide
of 59
Estefanía

## Slide 49: Efficiency of the converter
Voltages and powers at the converter’s input and output under STC.
Buck mode:
Slide
of 59
Estefanía

## Slide 50: Thermal test
Inductor and heat sink temperature varying with time.
Chart: Time [s]
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60
Coil | 18.2 | 20.2 | 28.3 | 35.9 | 42.8 | 47.1 | 53 | 57.6 | 62.3 | 66.5 | 70.2 | 74.2 | 76.6 | 78.8 | 81 | 83 | 86 | 88 | 90 | 93 | 94 | 95 | 98 | 98 | 99 | 102 | 104 | 104 | 104 | 104 | 104
Heat sink | 18.2 | 20 | 24.3 | 31.9 | 40.3 | 46.3 | 52.2 | 56.1 | 60.8 | 64.1 | 66.8 | 70 | 70.7 | 72.6 | 74.1 | 74.8 | 76.6 | 76.6 | 77.7 | 78.4 | 78.9 | 79.6 | 79.6 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81
Thermal camera showing hot and cold spots in the PCB.
Open-loop buck mode:
Slide
of 59
Estefanía

## Slide 51: Discussion

## Slide 52: Driver issues
Voltage spikes at gate
[3]
Slide
of 59
Nicolás

## Slide 53: Driver issues
[3]
Voltage spikes removed
Slide
of 59
Nicolás

## Slide 54: Voltage sensor issues
Design considered protection.
Positive peak voltage protection.
Output current limitation.
Slide
of 59
Nicolás

## Slide 55: Inductor
Loss of inductance.
Temperature increase.
Slide
of 59
Nicolás

## Slide 56: Software filtering
V and I measurements are noisy.
HW filtering at the output of the sensor is not enough.
Single pole LPF implemented.
Slide
of 59
Nicolás

## Slide 57: Future work
Hardware improvements.
Inductor design.
PCB optimization.
Converter’s efficiency.
V/I controller.
Slide
of 59
Thassilo

## Slide 58: Conclusion

## Slide 59: Thank you for your attention
Questions?
[4]

## Slide 60: References
[1] http://www.safegardgroup.com/blog/2017/07/27/solar-panel-disposal
[2] https://www.dgem.nl/nl/zonne-energie/opbrengstvariabelen-zonnepanelen
[3] MOSFET Gate Drive Circuit, Toshiba, 2018
[4] https://www.thermofisher.com/blog/mining/mining-metals-for-a-renewable-energy-future/