## Slide 1: DC-DC Converter for PV Module Integration
Group 760

## Slide 2: CONTENT
INTRODUCTION
CONVERTER DESIGN
MPPT ALGORITHM
TESTS RESULTS
DISCUSSION
CONCLUSION

## Slide 3: Introduction
[1]

## Slide 4: Motivation
Global need of transition towards clean energy.
Wind and solar energy production as fastest growing method in 2017.
I don’t know what else to say here.
Include picture.

## Slide 5: Existing problem
Partial shaded PV panel [2]
Mismatches:
Production tolerances
Partial shading
Cracks
Uneven aging

## Slide 6: What is a module integrated converter (MIC)?
Module integrated converter.
Is a part of each PV module.
Prevents mismatch losses.
Serial or parallel arrangements.

## Slide 7: MIC characteristics - Consider pros and cons
Allows individual maximum power point tracking.
Replaces bypass diode.
Higher system efficiencies achieved under mismatches.
Certain topologies allow bidirectionality.
Could imply lower efficiency under specific cases.
Are we saying anything else? Cost?

## Slide 8: Problem statement and objectives
How can a module integrated converter be designed to maximize
the PV power generation under real conditions?
Objectives:
Design a DC-DC converter for integration with a PV panel.
Implementation of an MPPT algorithm.
Hardware implementation of the MIC.
Test of the system and validation of the MIC.

## Slide 9
Converter Design

## Slide 10: System requirements
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Notes: How did we select the values
Input from PV panel
Output from inverter voltage and # of panels
# of panels from minimum and maximum duties
Ripples so we dont mess with the PV panel

## Slide 11: Selection of topology
Non-inverting buck-boost converter
Notes: Capabilities of both higher and lower output voltage
2 or 4 MOSFETs
Bidirectional opportunities
Lower (conduction) losses

## Slide 12: Passive components Sizing
Calculated using the ripples
Finding worst case conditions
Depends on switching frequency
Notes: Did a voltage sweep to determine worst case

## Slide 13: Passive components Sizing

## Slide 14: Passive components Selection
Minimum 20% margin was included
Reused inductor
Component | Theoretical value | Implemented value | Voltage rating
Input capacitor | 1540µF | 1880µF | 100V
Output capacitor | 130µF | 820µF | 250V
Inductor | 1.3mH | 1.93mH | -
Notes: Input cap is 4*470uF
Calculation mistakes lead to wrongly selected cout

## Slide 15: Power circuitry
High frequency capacitors.
Discharging resistors.
Protection diodes.

## Slide 16: Driving circuitry
Optocouplers for isolation.
Current limiting resistors.
Decoupling capacitors.

## Slide 17: Sensor circuitry
Notes: Optical unity-gain amplifier – voltage sensors
Hall effect – current sensor

## Slide 18: Power supplies
External supplies
Isolated 12V TRACO supplies
Linear 5V voltage regulator
LED at every supply line

## Slide 19: PCB layout
Considerations:
Hot and cold spots.
Isolations.
Interferences.
Others.

## Slide 20: Hot and cold sides
Clear separation of hot and cold sides.
Power side.
Control side, isolated.
Control side, non-isolated.

## Slide 21: EMI - EMC
Reduced current loops.
Hall sensor location.
Ground planes.

## Slide 22: Isolations
Isolation bridge.

## Slide 23: Others
Test points.
Other measuring points and user communication.
Heat sink location.
10mm power traces.

## Slide 24
MPPT Algorithm

## Slide 25: Perturb & Observe technique
P-V curve from a PV panel
1. Power evalution
> moving to MPP
< moving away from MPP
2. Voltage evalution
 | > | <
> | Voltage increase | Voltage decrease
< | Voltage decrease | Voltage increase
 | Voltage increase | Voltage decrease
 | Voltage decrease | Voltage increase

## Slide 26: Implementation
Block diagram of the system including the MPPT

## Slide 27: Initial MPPT implementation
Top figure: Conversion ratio for buck and boost modes.
Bottom figure: Mapping of the control variable for mode decision.
Mapping for mode decision:
If control variable < 0.5  Buck mode
If control variable 0.5  Boost mode
Incrementing control variable means decreasing PV voltage!

## Slide 28: Initial MPPT implementation
Finite state machine for P&O algorithm
Problems:
“If/else” structure difficult to find errors
Variable step required more complex code

## Slide 29: Fixed vs variable perturb step – Buck Mode
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.

## Slide 30: Fixed vs variable perturb step – Boost Mode
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.

## Slide 31: Final implementation
Main issues
Measurements were read too fast
Perturb step decreased after false positive MPP detection
Environmental variables’ changes

## Slide 32: Final implementation
Pmax
Vmax
Perturbation step & condition
change detection FSM

## Slide 33: Final implementation
3 seconds sim time
Boost, 8 panels

## Slide 34: Converter Design
Test Results

## Slide 35: Testing Overview
Model of the PV panel
Standard test conditions
Boundary between modes of operation
Sudden changes in environmental
Converter’s efficiency
…

## Slide 36: Test setup

## Slide 37: Test setup
PLECs model for interface with the RT Box.

## Slide 38: PV panel curves
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
[V] | 36.9 | 36.87 | 36.68 | 36.19
[A] | 8.14 | 6.49 | 4.86 | 3.23
[W] | 300.4 | 239.5 | 178.5 | 117
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
 | 36.9 | 36.87 | 36.68 | 36.19
 | 8.14 | 6.49 | 4.86 | 3.23
 | 300.4 | 239.5 | 178.5 | 117
P-V curves for T=25ºC and varying irradiance.
I-V curves for T=25ºC and varying irradiance.
Irradiance effect:
PV module datasheet (STC)

## Slide 39: PV panel curves
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
[V] | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
[A] | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
[W] | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
 | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
 | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
 | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
P-V curves for 1000 W/m2 and varying temperature.
I-V curves for 1000 W/m2 and varying temperature.
Temperature effect:

## Slide 40: Standard Test Conditions (STC)
Simulated results under STC with .
Buck mode:
Experimental results under STC with .

## Slide 41: Standard Test Conditions (STC)
Simulated results under STC with .
Boost mode:
Experimental results under STC with .

## Slide 42: Boundary between modes of operation
Panel’s voltage, current and power under STC with .
Buck mode (10 PV panels):
Duty cycles and voltages under STC with .
9.75 panels 10 panels
If T>25ºC  Boost

## Slide 43: Boundary between modes of operation
Panel’s voltage, current and power under STC with .
Boost mode (9 PV panels):
Duty cycles and voltages under STC with .
9.75 panels 9 panels
If T<25ºC  Buck

## Slide 44: Sudden change in irradiance
Simulated results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Experimental results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Buck mode :

## Slide 45: Sudden change in temperature
Simulated results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Experimental results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Buck mode :

## Slide 46: Comparison simulation and experiments
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s

## Slide 47: Efficiency of the converter
Voltages and powers at the converter’s input and output under STC.
Buck mode:

## Slide 48: Thermal test
Coil and heat sink temperature varying with time .
Chart: Time [s]
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60
Coil | 18.2 | 20.2 | 28.3 | 35.9 | 42.8 | 47.1 | 53 | 57.6 | 62.3 | 66.5 | 70.2 | 74.2 | 76.6 | 78.8 | 81 | 83 | 86 | 88 | 90 | 93 | 94 | 95 | 98 | 98 | 99 | 102 | 104 | 104 | 104 | 104 | 104
Heat sink | 18.2 | 20 | 24.3 | 31.9 | 40.3 | 46.3 | 52.2 | 56.1 | 60.8 | 64.1 | 66.8 | 70 | 70.7 | 72.6 | 74.1 | 74.8 | 76.6 | 76.6 | 77.7 | 78.4 | 78.9 | 79.6 | 79.6 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81
Thermal camera showing hot and cold spots in the PCB.
Open-loop buck mode :

## Slide 49: Discussion

## Slide 50: Driver issues
Voltage spikes at gate
[3]

## Slide 51: Driver issues
[3]
Voltage spikes removed

## Slide 52: Voltage sensor issues
Design considered protection
Positive peak voltage protection
Output current limitation

## Slide 53: Inductor
Loss of inductance
Temperature increase

## Slide 54: Software filtering
V and I measurements are noisy
HW filtering at the output of the sensor is not enough
Single pole LPF implemented

## Slide 55: Future work
Hardware improvements
Inductor design
PCB improvements
Converter’s efficiency
V/I controller

## Slide 56: Conclusion

## Slide 57: Conclusion
What went good
What went bad
What did we learn
Notes: Add something about the general intro?

## Slide 58: Thank you for your attention
Questions?
[4]

## Slide 59: References
[1] http://www.safegardgroup.com/blog/2017/07/27/solar-panel-disposal3/
[2] https://www.dgem.nl/nl/zonne-energie/opbrengstvariabelen-zonnepanelen
[3] MOSFET Gate Drive Circuit, Toshiba, 2018
[4] https://www.thermofisher.com/blog/mining/mining-metals-for-a-renewable-energy-future/