## Slide 1: DC-DC Converter for PV Module Integration
Group 760

## Slide 2: CONTENT
INTRODUCTION
CONVERTER DESIGN
MPPT ALGORITHM
TESTS RESULTS
DISCUSSION
CONCLUSION

## Slide 3: Introduction
[1]

## Slide 4: Motivation
Global need of transition towards clean energy.
Wind and solar energy production as fastest growing method in 2017.
I don’t know what else to say here.
Include picture.

## Slide 5: Existing problem
Partial shaded PV panel [2]
Mismatches:
Production tolerances
Partial shading
Cracks
Uneven aging

## Slide 6: What is a module integrated converter (MIC)?
Module integrated converter.
Is a part of each PV module.
Prevents mismatch losses.
Serial or parallel arrangements.

## Slide 7: MIC characteristics - Consider pros and cons
Allows individual maximum power point tracking.
Replaces bypass diode.
Higher system efficiencies achieved under mismatches.
Certain topologies allow bidirectionality.
Could imply lower efficiency under specific cases.
Are we saying anything else? Cost?

## Slide 8: Problem statement and objectives
How can a module integrated converter be designed to maximize
the PV power generation under real conditions?
Objectives:
Design a DC-DC converter for integration with a PV panel.
Implementation of an MPPT algorithm.
Hardware implementation of the MIC.
Test of the system and validation of the MIC.

## Slide 9: Converter Design
Converter Design

## Slide 10: System requirements
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Converter input | 
 | 300.4 [W]
 | 45 [V]
 | 8.67 [A]
Converter output | 
 | 90 [V]
 | 24 [V]
 | 12.5 [A]
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Ripples | 
 | 0.5 [%]
 | 0.1 [%]
 | 10 [%]
PV system specification | 
Minimum string length | 4
Maximum string length | 15
Notes: How did we select the values
Input from PV panel
Output from inverter voltage and # of panels
# of panels from minimum and maximum duties
Ripples so we dont mess with the PV panel

## Slide 11: Selection of topology
Non-inverting buck-boost converter
Notes: Capabilities of both higher and lower output voltage
2 or 4 MOSFETs
Bidirectional opportunities
Lower (conduction) losses

## Slide 12: Passive components Sizing
Calculated using the ripples
Defining worst case conditions
Depends on switching frequency
Here is the unit of the diagram missing
Notes: Did a voltage sweep to determine worst case

## Slide 13: Passive components Sizing

## Slide 14: Passive components Selection
Minimum 20% margin was included
Reused inductor
Component | Theoretical value | Implemented value | Voltage rating
Input capacitor | 1540µF | 1880µF | 100V
Output capacitor | 130µF | 820µF | 250V
Inductor | 1.3mH | 1.93mH | -
Notes: Input cap is 4*470uF
Calculation mistakes lead to wrongly selected cout

## Slide 15: Power circuitry
Discharging resistors.
Protection diodes.
High frequency capacitors.

## Slide 16: Power circuitry
Discharging resistors.
Protection diodes.
High frequency capacitors.

## Slide 17: Driving circuitry
Optocouplers for isolation.
Decoupling capacitors.
Current limiting resistors.

## Slide 18: Sensors
Measures input voltage and current
Sensors includes isolation
Notes: Optical unity-gain amplifier – voltage sensors
Hall effect – current sensor

## Slide 19: Power supplies
External supplies
Linear 5V voltage regulator
Isolated 12V TRACO supplies
LED at every supply line
INSERT PICTURES OF TRACOS AND LEDS

## Slide 20: PCB layout
Considerations:
Hot and cold spots.
Isolations.
Interferences.
Others.

## Slide 21: Hot and cold sides
Clear separation of hot and cold sides.
Power side.
Control side, isolated.
Control side, non-isolated.

## Slide 22: EMI - EMC
Reduced current loops.
Hall sensor location.
Ground planes.

## Slide 23: Isolations
Isolation bridge.

## Slide 24: Others
Test points.
Other measuring points and user communication.
Heat sink location.
10mm power traces.

## Slide 25: Converter Design
MPPT Algorithm

## Slide 26: Perturb & Observe technique
P-V curve from a PV panel
1. Power evalution
> moving to MPP
< moving away from MPP
2. Voltage evalution
 | > | <
> | Voltage increase | Voltage decrease
< | Voltage decrease | Voltage increase
 | Voltage increase | Voltage decrease
 | Voltage decrease | Voltage increase

## Slide 27: Implementation
Block diagram of the system including the MPPT

## Slide 28: Initial MPPT implementation
Top figure: Conversion ratio for buck and boost modes.
Bottom figure: Mapping of the control variable for mode decision.
Mapping for mode decision:
If control variable < 0.5  Buck mode
If control variable 0.5  Boost mode
Incrementing control variable means decreasing PV voltage!

## Slide 29: Initial MPPT implementation
Finite state machine for P&O algorithm
Problems:
“If/else” structure difficult to find errors
Variable step required more complex code

## Slide 30: Fixed vs variable perturb step – Buck Mode
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.

## Slide 31: Fixed vs variable perturb step – Boost Mode
Oscillations around the MPP with fixed perturb step under STC.
Oscillations around the MPP with variable perturb step under STC.

## Slide 32: Final implementation
Main issues
Measurements were read too fast
Perturb step decreased after false positive MPP detection
Environment’s variables changes

## Slide 33: Final implementation
Pmax
Vmax

## Slide 34: Final implementation
3 seconds sim time
Boost, 8 panels
a

## Slide 35: Test Results

## Slide 36: Testing Introduction
Model of the PV panel
Standard test conditions
Boundary between modes of operation
Sudden changes in environmental
Converter’s efficiency
…

## Slide 37: Test setup

## Slide 38: PV panel curves
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
[V] | 36.9 | 36.87 | 36.68 | 36.19
[A] | 8.14 | 6.49 | 4.86 | 3.23
[W] | 300.4 | 239.5 | 178.5 | 117
 | 1000 W/m2 | 800 W/m2 | 600 W/m2 | 400 W/m2
 | 36.9 | 36.87 | 36.68 | 36.19
 | 8.14 | 6.49 | 4.86 | 3.23
 | 300.4 | 239.5 | 178.5 | 117
P-V curves for T=25ºC and varying irradiance.
I-V curves for T=25ºC and varying irradiance.
Irradiance effect:

## Slide 39: PV panel curves
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
[V] | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
[A] | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
[W] | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
 | 15ºC | 25ºC | 35ºC | 45ºC | 55ºC
 | 41.45 | 36.9 | 32.59 | 28.34 | 24.23
 | 7.33 | 8.14 | 8.85 | 9.59 | 10.12
 | 304.3 | 300.4 | 289.1 | 270.7 | 245.8
P-V curves for 1000 W/m2 and varying temperature.
I-V curves for 1000 W/m2 and varying temperature.
Temperature effect:

## Slide 40: Standard Test Conditions (STC)
Simulated results under STC with .
Buck mode:
Experimental results under STC with .

## Slide 41: Standard Test Conditions (STC)
Simulated results under STC with .
Boost mode:
Experimental results under STC with .

## Slide 42: Boundary between modes of operation
Panel’s voltaje, current and power under STC with .
Buck mode:
Duty cycles and voltages under STC with .

## Slide 43: Boundary between modes of operation
Panel’s voltaje, current and power under STC with .
Boost mode:
Duty cycles and voltages under STC with .

## Slide 44: Sudden change in irradiance
Simulated results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Experimental results for 1000 - 800 W/m2 and constant temperature T=25ºC.
Buck mode:

## Slide 45: Sudden change in temperature
Simulated results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Experimental results for 25 - 15 ºC and constant irradiance 1000 W/m2.
Buck mode:

## Slide 46: Efficiency of the converter
Voltages and powers at the converter’s input and output in Buck mode under STC.

## Slide 47: Comparison simulation and experiments
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Buck STC | Simulation | Experiment
 | 99.96% | 97.72%
 | 2 s | 10 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Boost STC |  | 
 | 99.82% | 97.32%
 | 4 s | 21 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 1000 - 800 W/m2 |  | 
 | From 99.81% to 99.70% | From 95.96% to 93.78%
 | 0.5 s | 6.6 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s
Buck 25 - 15 ºC |  | 
 | From 99.81% to 99.90% | From 99.20% to 98.40%
 | 2 s | 4.1 s

## Slide 48: Discussion

## Slide 49: Driver issues
Voltage spikes at gate
[3]

## Slide 50: Driver issues
[3]
Voltage spikes removed

## Slide 51: Voltage sensor issues
Design considered protection
Positive peak voltage protection
Output current limitation

## Slide 52: Inductor
Loss of inductance
Temperature increase

## Slide 53: Software filtering
V and I measurements are noisy
HW filtering at the output of the sensor is not enough
Single pole LPF implemented

## Slide 54: Future work
Hardware improvements
Inductor design
PCB improvements
Converter’s efficiency
V/I controller

## Slide 55: Conclusion

## Slide 56: Conclusion
What went good
What went bad
What did we learn
Notes: Add something about the general intro?

## Slide 57: Thank you for your attention
Questions?
[4]

## Slide 58: References
[1] http://www.safegardgroup.com/blog/2017/07/27/solar-panel-disposal3/
[2] https://www.dgem.nl/nl/zonne-energie/opbrengstvariabelen-zonnepanelen
[3] MOSFET Gate Drive Circuit AN, Toshiba, 2018
[4] https://www.thermofisher.com/blog/mining/mining-metals-for-a-renewable-energy-future/