## Slide 2: Bypass diodes vs MICs
Single bypass diode protects one sub-string (20 cells)
If high current flows through shaded cell  Power is consumed instead of produced!
Avoid hot-spots because the power consumed by the cell heats it up.
20% irradiance difference  bypass diode ON
Higher power losses than with MICs
Sub-string

## Slide 3: Bypass diodes vs MICs
Why using MICs improves power extraction?
Demonstration example: shaded cell at 80% irradiance
1st option: Bypass diode ON  9*10% + 1*6.6% = 96.6%
2nd option: Reduce current to 80% 80% of full power
3rd option: MPPT tracker  9*10% + 1*8% = 98%
Using MICs in each PV module  Increases power by 1.4%

## Slide 4: Bypass diodes vs MICs
Why using MICs improves power extraction?
Demonstration example: 30% shaded region
1st option: Bypass diodes ON  9*10% + 1*0% = 90%
2nd option: Reduce current to 70% 70% of full power
3rd option: MPPT tracker  9*10% + 1*7% = 97%
Using MICs in each PV module  Increases power by 7%

## Slide 5: Limitations of single diode PV model
ideal
practical
Not enough with the ideal cell model to define the I-V characteristics of a solar panel because it is an array of series connected cells so it’s necessary to include Rs and Rp!

## Slide 6: Limitations of single diode PV model
Rs  sum of several structural resistances of the PV panel.
Rp  due to the leakage current of the p-n junction and depends on the fabrication method of the cell.
Rp has very high value and Rs very low value (in some cases can be neglected)

## Slide 7: Limitations of single diode PV model
Double diode model:
Extra diode in parallel included to provide an EVEN more accurate I-V characteristic curve
“This model considers the difference in flow of current at low current values due to charge recombination in the semicondictor’s depletion región” (DON’T GET THIS :/)
Higher accuracy with this model BUT increase difficulty to solve the equation  Single diode model is preferred!