## Slide 1: HIGH VOLTAGE ENGINEERING ABB EMF 72KV INDUCTIVE VOLTAGE TRANSFORMER
Intro760
pramod , Ariya, unni, marcos

## Slide 2: Introduction
Power systems equipment should withstand rated voltage as well as over voltages
This is ensured by carrying out suitable tests on the equipments before commissioning
This study involves assessment of insulation quality of ABB emf 72kv inductive voltage transformer

## Slide 3: Standard terms used to classify high voltage transformers
Rated primary voltage
Rated secondary voltage
Transformation ratio
Rated voltage factor
Insulation
Accuracy class
Thermal limit burden
Ambient temperature
Creepage distance
Flashover distance
Pollution level
Notes: A high Voltage transformer is generally intended to step down the voltage level from a high level to a safe low level for subsequent connections to measuring and control(relay) Circuits.

## Slide 4: Abb emf 72kv transformer
1 | Primary terminal | 9 | Expansion system
2 | Oil level sight glass | 10 | Paper insulation
3 | Oil | 11 | Tank
4 | Quartz filling | 12 | Primary winding
5 | Insulator | 13 | Secondary winding
6 | Lifting lug | 14 | Core
7 | Secondary terminal box | 15 | Secondary terminals
8 | Neutral end terminal | 16 | Ground Connection

## Slide 5
Design features and advantages
Windings – double enamelled
Core – very low flux
Impregnation
Aluminium tank – resistance to corrosion
Expansion system
Designed to counter ferroresonance
Designed for wide climatic changes
Quartz filling
Seismic strength

## Slide 6
specifications

## Slide 7: Measure transfer ratio full range
Measure low and high terminal voltages

## Slide 8: Measure transfer ratio full range
Calculate the slope of the graph
n ≈

## Slide 9: Impulse voltage
          Three types of lightning impulse
                - LI chopped on the front
                - Full LI
      - LI chopped on the tail
Type b circuit is more preferred

## Slide 10: Impulse voltage
          Three types of lightning impulse
                - LI chopped on the front
      - Full LI
      - LI chopped on the tail
Type b circuit is more preferred

## Slide 11: 50 percent Breakdown voltage
          Randomness of the result
          V50 can be obtained from CDF
Multi-level method is used

## Slide 12: 50 percent Breakdown voltage
          V50 ≈ 53 kV
          Limitation : number of test

## Slide 13: Partial discharge measurement
Two types
Internal discharge
External discharge
1. Corona
2. Surface discharge
Responsible for losses and degradation of insulation

## Slide 14: Internal discharge
Caused by
Voids in solid dielectric
Lower permittivity in void than surrounding media leading to higher stress and breakdown

## Slide 15: Internal discharge (contd)
C3>>C1>>C2
Voltage across C1=C2/(C1 + C2) ∗ um sin(wt)
Um> critical voltage discharge occurs
Higher the voltage multiple discharges depending on du/dt
Voltage across C1 in phase with applied voltage so discharge at zero crossings

## Slide 16: External discharge
Corona- occurs in gaseous medium under non uniform electric field
Surface discharge- along surface of two dielectrics of different permittivities
Equivalent scheme

## Slide 17: External discharge(contd)
R>>1/wc1
The voltage across C1 U10 = um sin(wt − π/2)/wc*1r2
Discharge at um>critical voltage
Multiple discharges for higher um based on +-du/dt
Discharge frequency highest at maximum du/dt
Since voltage across capacitor lagging it occurs near peak values

## Slide 18: Test setup

## Slide 19: Test setup(contd)
Apparent charge measurement followed
Ck –coupling capacitor compensates for charge drop in test specimen if(ck > ca )
Q value indication of partial discharge

## Slide 20: Test specimens
ABB transformer
Homemade capacitor
Rod to plane electrode

## Slide 21: Results and analysis
ABB transformer – tested at 45kv
No measurable pd pulses attributed to noise

## Slide 22: Results and analysis (contd)
Homemade capacitor –tested at 28 kV

## Slide 23: Results and analysis (contd)
Rod to plate electrode –tested at 24 kV
As discussed pd at peaks of supply voltage

## Slide 24: Loss angle measurement
Real dielectric have losses
      -P1: conductive losses
      -Pp: polarization losses
      -Pi: ionization losses
Phasor diagram

## Slide 25
Dielectric Spectroscopy
Schering bridge
Cx Device under test
Cn Gas capacitor

## Slide 26: Results
Abb Transformer Home made Pure Capacitor
“Ionization knee”
It could be indication of partial discharges

## Slide 27: Dielectric spectroscopy
-Moisture can damage transformers and shorten its lifetime.
This method:
Test the properties of the insulation over wide frequency range (0.01-1000 Hz) in order to determine the moisture content.

## Slide 28: Results

## Slide 29: Interpretations
Maik Koch, Michael Krueger and Markus Puetter; Advanced Insulation Diagnostic
by Dielectric Spectroscopy, OMICRON

## Slide 30: Tak!