## Slide 1: HV mini-project seminar
High Voltage engineering course
Giustino – Cormac – Ying – Saioa – Pablo - Nicola
31st October, 2012

## Slide 2: Description of voltage transformer
ABB EMF 72 Transformer

## Slide 3: Description of voltage transformer
Rated data
Voltage Tranformer | ABB EMF 72
Insulation Level 140-350 kV | High Volt. for equipment 72 kV 50 Hz
Standard IEC 186 | Voltage factor (Vf) 1.9/8h
Total mass 190 kg | Year of manufacture 1998
A-N | 1a-1n | 2a-2n | da-dn
60000V / √3 | 110V / √3 | 110V / √3 | 110V / √3
Load | 1 – 15 VA | 1 – 65 VA | 75 VA
Class | 0,2 | 0,2 | 3P

## Slide 4: Description of voltage transformer
Conductor
SF6
Porcelain Bushing Insulators
External Insulator
Internal Insulator
Oil+Paper

## Slide 5: Transfer Ratio
The primary winding of the transformer is connected directly to the high voltage source transformer via aluminium conductors
Output voltage measured at secondary winding of transformer using a multimeter

## Slide 6: Transfer Ratio
Rated transfer ratio
Ideal transformer
Transfer Ratio

## Slide 7: Transfer Ratio

## Slide 8
Lightning Overvoltage Test
What’s Lightning overvoltage?
Originated by lightning stroke on the phase wires of overhead line or busbars
Caused by switching phenomena

## Slide 9
Waveforms of Lightning Impulse
Figure 1 General shapes and definitions of lightning impulse (LI)
(a)Full LI (b) LI chopped on the tail (c)LI chopped on the front.
T1: front time T2: time to half-value Tc: time to chop o1: virtual origin
Lightning Overvoltage Test

## Slide 10
Lightning Overvoltage Test
What should be done in the test?
Build a circuit that can generate lightning impulses and be able to control their waveforms.
Apply the generated lightning impulses to the insulation part of the transformer and test how much it can undertake.
Connect the surge arrester to the insulation and test it.

## Slide 11
Lightning Overvoltage Test
Impulse voltage generator circuits

## Slide 12
Impulse voltage generator circuits
Lightning Overvoltage Test

## Slide 13
Lightning Overvoltage Test
Experiment Setup

## Slide 14
Experimental Results
Lightning Overvoltage Test

## Slide 15
Lightning Overvoltage Test
Experimental Results

## Slide 16
Lightning Overvoltage Test
Experimental Results

## Slide 17
Lightning Overvoltage Test
Experimental Results

## Slide 18
Lightning Overvoltage Test
Experimental Results

## Slide 19
Lightning Overvoltage Test
Experimental Results

## Slide 20: Dielectric Loss Angle Measurement
What is it?
Non destructive High-Voltage isolation test.
Why is it measured?
Dielectrics and isolating materials can be characterized by its natural polarization phenomena.
How can it be determined?
In the Frequency domain it can be model as a capacitance [C] and a power dissipation magnitud quantified with the loss factor [tan δ].

## Slide 21: LAB SET-UP
Schering Bridge
Dielectric Loss Angle Measurement
Transformer used in previous exeriments
.
Frequency: 50Hz
Theoreticaly
In the lab
Measure of C and tan δ by comparing with Cn
Cn: gas-filled capacitor with very low loss
Frequency for which the system has been designed

## Slide 22
Dielectric Loss Angle Measurement
1st Measure: Measuring the primary of the transformer.
The capacitance and the loss angle are bigger than expected.
NOT VALID MEASURE

## Slide 23
2nd Measure: Measuring the secondary.
Dielectric Loss Angle Measurement

## Slide 24
3rd Measure: Adding a home made Capacitor
The maximum voltage that the capacitor can handle: 25kV.
Dielectric Loss Angle Measurement

## Slide 25: Partial discharges measurement
What is a partial discharge?
Partial discharges (PD) can be defined as discharges only partially short circuiting an insulating media between two electrodes with different potential.
Why do we measure partial discharges?
It has a significant effect on the life of insulation. Every discharge event causes a deterioration of the material by energy impact.

## Slide 26: Partial discharges measurement
Types of Partial Discharges (PD):
External Partial Discharges
  Corona: type of PD in gaseous media (audible noise)
  Surface discharges: PD in boundaries between different dielectrics (i.e. gas/oil)
Internal Partial Discharges
PD in cavities in solid or liquid dielectrics

## Slide 27: Partial discharges measurement
Laboratory setup
At the moment when the PD appears, the sharpen part will be HV side

## Slide 28: Partial discharges measurement
Experimental results (HQQ 3-D plot)
External partial discharges:
Corona effect or surface discharges
They occur:
At the peaks of the Voltage waveform (90 or 270º)
A->K (90º) / K->A (270º)

## Slide 29: Partial discharges measurement
Experimental results (HQQ 3-D plot)
External PD
Internal PD
Internal partial discharges:
In voids or cavities
They occur:
At 0 / 180 / 360º

## Slide 30: Dielectric spectroscopy test
- Spectroscopy is the measurement of the parameters in the frequency of isolation
- The perfect isolation has a 90°

## Slide 31: LABORATORY SETUP

## Slide 32: RESULTS

## Slide 33: RESULTS
Moisture content: 4,8 %
Oil conductivity: 35 aS/m

## Slide 34: Partial discharges measurement
References
[1] E. Kuffel, W.S.Zaengl and J. Kuffel, High Voltage Engineering: Fundamentals,second edition 2000, Newnes, ISBN 0 7506 3634 3.
Lectures and laboratory notes. High voltage engineering course. Aalborg University.

## Slide 35: Partial discharges measurement
Thanks for
your attention!